ORDINANCE NO. 51
ORDINANCE OF THE HYDESVILLE COUNTY WATER DISTRICT,

TO PROVIDE FOR AN AMENDMENT TO ORDINANCE N0. 23,
RELATING TO CROSS CONNECTION CONTROL

TO THE DISTRICT WATER SYSTEM.

Be it ordained by the Board of Directors of the Hydesville County Water District, Humboldt County, as follows:


1.  Paragraph 155 of Article 8 is hereby amended to read as follows:

155 Cross-Connections Prohibited
(a) Cross-Connections Prohibited

Except as provided below, all cross-connections, whether or not they are controlled by automatic devices such as check valves or by hand operated mechanisms such as gate valves or stop clocks, are prohibited. Failure on the part of persons, firms, or corporations to discontinue the use of all cross-connections and to physically separate cross-connections is sufficient cause for the immediate discontinuance of public water services to the premises.
(1)  The failure of the owner or occupant to cooperate in the installation, maintenance, testing or inspection of backflow prevention device is required by the ordinance and the District may have services discontinued after service of 24 hours’ notice.
(g) Inspections
Backflow preventions devices must be inspected and tested annually or more often when inspection fee will be charged. The device must be repaired, overhauled, or replaced whenever it is found to be defective. Inspections and tests must be made by a certified cross-connection specialist or by the District’s personnel and the device tagged. Repairs will be made at the expense of the owner or occupant.
(1) Required backflow prevention assembly maintenance, repair or replacement will happen within 30 days after identification.

(2) All individuals who test backflow prevention assemblies within the Hydesville County Water District must be registered with the District and appear on the District’s approved tester list. Customers may only use testers from this approved list to ensure compliance with District policy and CCCPH requirements. Each tester must provide proof of current certification and documentation verifying annual calibration of their test equipment (within the past twelve months) to the District’s office. Certified testers are required to submit copies of all completed backflow prevention assembly test results to the District for recordkeeping in accordance with its Cross-Connection Control Program §§3.3 and 3.5.1

(3) All individuals who test backflow prevention assemblies for Hydesville County Water District must:

(a) Hold valid certification from an ANSI-accredited or State Water Board-recognized organization.
(b) Each tester’s field kit must be maintained in accurate working conditions and routinely verified or calibrated to ensure reliability of test results.

(c) Certified testers are required to submit copies of all backflow prevention assembly test reports to the District for record keeping and program compliance
(j) Records of Cross-Connection Control Program
Hydesville County Water District maintains records related to its Cross-Connection Control Program. Records include backflow prevention assembly test reports, hazard assessments, corrective action notices, customer notifications, approved tester registration information, and documentation of tester certifications and equipment calibrations. Additional records include Cross-Connection Control Program revisions, correspondence with regulatory agencies, and any incident reports related to backflow or contamination events. All records are retained for a minimum of three (3) years and are available for review by the State Water Resources Control Board, Local Primacy Agency, or other authorized representatives upon request.

(k) Hazard Assessments
The Hydesville County Water District will incorporate the recommendations of each hazard assessment no later than 30 days after the initial hazard assessment is complete.

(1) The District will conduct ongoing hazard assessments of each service connection at least every 5 years after the initial hazard assessment is complete.

2. The District may, in its sole discretion, have the option of adjusting the deadline requirements in which ordinance requires the customer to repair or replace the back flow prevention device on a case-by-case basis. To which the customer must present its case or hardship to the board at a regularly scheduled Board meeting before the end of the notice period.
3.The Board also reserves the right to institute a grace period (in addition to, and separate from, the initial request as described above) for no longer than 6 months from the date the board approves the grace period request.

4.  Paragraph 155 of Article 8 is hereby amended.

5. This ordinance shall take effect _________________.  Passed and adopted _______________

 by the following votes:  




    Ayes: ________________


                Noes: ________________

________________________________               ATTEST: __________________________

Randall Stone,
Chairman



         Megan Lowe, Secretary of the Board

Board of Directors




         Hydesville County Water District
Hydesville County Water District                                           
